Typical Specifications

Seismically Certified SF6 insulated Switchgear – Model SPRAM

Part 1-GENERAL

  - DESCRIPTION

- The switch shall consist of manually operated load interrupting, SF6 insulated linear puffer switches

- The switch shall be certified for use in seismically active areas

- The switch shall be certified for use in OSHPD (Office of Statewide Health Planning and Development) projects for healthcare facilities in the State of California.  The OSHPD application number on file is OSP-0157-10

  - QUALITY ASSURANCE

- Manufacturer Qualifications:  The chosen manufacturer shall have at least 40 years experience in manufacturing SF6 insulated medium voltage switchgear. The manufacturer of the switches shall be completely and solely responsible for the performance of the load break switch as well as the complete integrated assembly as rated.

- The manufacturer shall furnish certification of ratings of the load break switch and the integrated switch assembly upon request.

- The switch shall comply with requirements of the latest revision of applicable industry standards, including IEEE C37.72, IEEE C37.74, ANSI/IEEE 386, IEC 60265-1

- The switches must be designed per the guidelines of ASCE (American Society of Civil Engineers) standard 7-05 Chapter 13.  These guidelines cover the design of non structural components installed in a building.  The switches must also undergo a test regime specified by ICC-ES-AC-156 (International Code Council Evaluation Services Acceptance Criteria) which specifies the shaker table test inputs applied to the switches.

- The switch manufacturer shall be ISO 9001:2008 and ISO 14001:2004 certified.

  - DELIVERY, STORAGE, AND HANDLING

- Load Break switches shall be shipped preassembled at the factory. No field assembly shall be required.

- The contractor, if applicable, shall handle, transfer and move the switches in accordance with manufacturer’s recommendations.

PART 2-PRODUCTS

2.1 SWITCH CONFIGURATION

- Each switch shall be equipped with a 3-phase load switch ways as indicated on the one-line diagram.

- Switches shall be designed for front access to operators and bottom access to operators (six ways max), as indicated.

2.2 SWITCH CONSTRUCTION

- General

Switch contacts and cable entrance terminations shall be contained in a single welded mild steel tank with entrances internally connected by copper conductors. Construction shall be a deadfront design. Switches shall be shipped factory filled with SF6 gas conforming to ASTM D-2472. Switch tanks shall be painted ASA70 light gray using a corrosion-resistant epoxy paint.

- Load Break Puffer Switch

Each switching way is to be equipped with an internally mounted operating mechanism capable of providing quick-make, quick-break operation in either switching direction. The mechanism must be capable of delivering sufficient torque and shall be provided with latches for each position to assure load interrupting, fault closing and momentary ratings. All switch positions are to be clearly identified, padlockable and adaptable to keylock schemes. The operating mechanism shall be actuated from outside the switch tank with an operating handle. The operating shaft shall be made of stainless steel for maximum corrosion resistance. A double “O” ring type operating shaft seal shall be used for a leak resistant, long life seal. Switch contacts shall be a tulip-bayonet design and made of plated, high-conductivity copper alloy with arcing tips of copper/tungsten alloy to assure permanent low resistance and to avoid sticking during operations. The contacts shall be designed such that arcing does not occur in the area of main current interchange and contact pressure will increase with increased current flow. The stationary contacts shall be supported independent of the cable entrance bushings, eliminating possible misalignment. The contact nozzle shall have a converging/diverging geometry which improves the flow of SF6 into the arc zone. Contact travel shall be a minimum of 3 inches and have sufficient open contact separation to assure efficient arc extinction and to withstand field DC testing levels and maintain BIL levels. Switch contacts shall be clearly visible in the open position through viewing windows. Auxiliary blades used for load interruption are not acceptable.

2.3 DESIGN RATINGS

A.  Load Break Switches

The switch shall be rated: (choose appropriate column)

| SELECTION OF RATINGS | IEEE/IEC |  |  |
| --- | --- | --- | --- |
| Maximum Design Voltage, kV | 15.5 | 27 | 38 |
| Impulse Level (BIL) Voltage, kV | 110 | 125 | 150 |
| Continuous Current, Amperes | 900 | 900 | 630 |
| Load break Current, Amperes | 900 | 900 | 630 |
| One Minute Withstand (dry), AC kV | 35 | 60 | 70 |
| Production Test Rating | 34 | 40 | 50 |
| 15 Minute Withstand, DC kV | 53 | 78 | 103 |
| Momentary Current, kA, ASYM | 40 | 40 | 40 |
| Fault-Close Current, kA, ASYM | 40 | 40 | 40 |
| One Second Current, kA, SYM | 25 | 25 | 25 |
| Mechanical Endurance, Operations | 2000 | 2000 | 2000 |
| Load break Operations at 600 Amperes | 1200 | 1200 | 1200 |
| Open gap BIL withstand, kV | 200 | 200 | 200 |

2.4 CABLE ENTRANCES

Cable entrances shall be tested to IEEE 386 and be, as indicated on the switch drawing:

- ____900 amp rated apparatus bushing (note to specifier:  15kV and 25kV only)

- ____600 amp G&W Quick-Change disconnectable apparatus bushing (note to specifier:  35kV only)

- ____200 amp Deepwell bushing.

2.5 ENCLOSURE

Enclosures shall be made of 12 gauge galvanized steel and manufactured to ANSI C37.72 and C57.12.28 standards. The enclosure shall be mounted independent of the switch allowing removal for ease of cable installation or future replacement if required. Enclosures shall be tamper=resistant incorporating hinged access doors with pentahead locking bolts and provisions for padlocking. The enclosure shall be provided with lifting provisions and painted with a Munsell 7.0GY3.29/1.5 green finish.

2.6 FACTORY PRODUCTION TEST

The bulk SF6 gas supply and each individual switch shall be tested for moisture content. Each individual switch shall undergo a mechanical operation check and a leak test. The switch shall be factory filled with SF6 and AC hi-pot tested one minute phase-to-phase, phase-to-ground and across te open contacts. Circuit resistance shall be checked on all ways. Switches will be shipped factory filled with SF6 gas. Tank shall be designed to withstand 15 psig internal pressure and an external pressure of 14 psig without affecting the performance of the switch.

2.7 STANDARD COMPONENTS

The following shall be included as standard:

- Welded steel tank painted light gray with stainless steel and brass fasteners.

- Lifting provisions.

- Gas pressure gauge and fill valve.

- Grounding provisions for switch tank and all cable entrances.

- Stainless steel three line diagram and corrosion-resistant nameplates.

- Parking stands

- Switch operating handle(s) with padlock provision and end stops.

- Seismic bracing per the design requirements of ASCE 7-05 Chapter 13

- Load Break switches shall use angled bushing style for compact footprint

- 42” minimum bushing height with 90” high enclosure

2.8 OPTIONS

The following shall are available as options:

____ Low pressure alarm to monitor gas pressure remotely

____ Form C auxiliary contact to remotely monitor switch contact position

____ Junction box to wire low pressure alarm and auxiliary contacts

2.9 SEISMIC TESTING

The switch must be tested to ICC-ES-AC-156 and designed in accordance to ASCE 7-05 Chapter 13.  The switch must be approved for use in OSHPD project.  The application number on file with OSHPD is OSP-0157-10.

2.10 LABELING

A. Hazard Alerting Signs

The exterior of the padmounted enclosure (if furnished) shall be provided with “Warning--Keep Out--Hazardous Voltage Inside--Can Shock, Burn, or Cause Death” signs. Each unit of switchgear shall be provided with a “Danger--Hazardous Voltage--Failure to Follow These Instructions Will Likely Cause Shock, Burn, or Death” sign. The text shall further indicate that operating personnel must know and obey the employer’s work rules, know the hazards involved, and use proper protective equipment and tools to work on this equipment. Each unit of switchgear shall be provided with a “Danger--Keep Away--Hazardous Voltage--Will Shock, Burn, or Cause Death” sign.

B.Nameplates, Ratings Labels, and Connection Diagrams

Each unit of switchgear shall be provided with a nameplate indicating the manufacturer’s name, catalog number, model number, date of manufacture, and serial number. Each unit of switchgear shall be provided with a ratings label indicating the following: voltage rating; main bus continuous raing; short-circuit rating; fault interrupter ratings including interrupting and duty-cycle fault-closing; and load break switch ratings including duty-cycle fault-closing and short-time.

C. an OSHPD Certification label must be affixed to each switch which includes the OSHPD certification number and test parameters.